## 1
[7 empty] | MASS FLOW METER |  |  |  | SHEET |  | 1 OF 1 | OF
[11 empty] | SPEC. NO. |  |  |  | REV.
0
[7 empty] | (Thermal Mass Flow Meter) |  |  |  | CONTRACT |  |  |  | DATE
CLIENT |  | : | SK Technopack | [11 empty] | 2017.08.30
PROJECT |  | : | Cheonan Factory |  |  |  | NO | BY | DATE | REVISION | REQ. or P.O
JOB NO. |  | : |  |  |  |  | 0 |  | 2017.08.30 | FOR APPROVAL
LOCATION |  | : | Compressed & Process Air line | [7 empty] | BY | CHK'D |  |  | APPR.
GENERAL
1 | Tag Number |  |  |  |  | FT-
2 | Quantity(Set) |  |  |  |  | 1
3 | Service
4 | Line No. & Sch. No |  |  |  |  | 6"(150A) & 10
SERIVCE CONDITION
5 | Fluid |  |  |  |  | Compressed Air
6 | Flow Rate(Nm3/h) |  |  |  | Nor. | 80
Max.
7 | Pressure(kg/cm2.G) |  |  |  | Nor. | 7
Max.
8 | Temperature(℃) |  |  |  | Nor. | 20
Max.
9 | Sp/gr(kg/m3) |  |  |  |  | 1000
10 | Viscosity |  |  |  |  | N/A
11 | Molecular Weight |  |  |  |  | 29
FLOW SENSOR
11 | Type |  |  |  |  | Insertion
12 | Velocity(m/s) |  |  |  |  | 0.01~66.2
13 | Insert Length (L09) |  |  |  |  | 330mm
14 | Connection Type |  |  |  |  | Compression Fitting
15 | Connection Size & Rating |  |  |  |  | 1"PT + 3/4" Tube & 10Bar
16 | Material |  |  | Sensor Probe |  | Ceramic+SUS303
|  |  |  | Protection tube |  | SUS303
|  |  |  | Comp' Fitting |  | SUS316
17 | Temperature(℃) |  |  |  | Min. | -40
[5 empty] | Max. | 150
18 | Accuracy |  |  |  |  | ±0.5% F.S(Reading:+/-0.5% F.S)
19 | Flow Direction |  |  |  |  | Horizontal -> Free
TRANSIMITTER
20 | Type |  |  |  |  | Program Smart
21 | Power Input |  |  |  |  | 100-240VAC, max. 10watts
22 | Output Signal |  |  |  |  | 4~20mA DC & Pulse
23 | Interface |  |  |  |  | MOD-BUS RS-485
24 | Enclosure |  |  |  |  | IP 67
25 | Display(LCD) |  |  |  |  | Flow Rate & Total, Velocity
26 | Housing Mat'l |  |  |  |  | Al.Casting
27 | Scale Range |  |  |  |  | 0 ~ 80 Nm3/min
28 | Compensation : Press' & Temp' |  |  |  |  | Yes
ACCESSORIES
29 | Compression Fitting |  |  |  |  | Yes
30 | Remote Cable(30m) |  |  |  |  | Not
31 | Ball Valve Assembly |  |  |  |  | Yes
32 | Option 1 :
MANUFACTURER
33 | M.F.R |  |  |  |  | Golden Rules
34 | Model No. |  |  |  |  | KC-2610GI-L12
Notes :
MASS FLOW METERS
Golden Rules Co., Ltd.