## 1
[7 empty] | MASS FLOW METER |  |  |  | SHEET |  |  | 1 OF 1 | OF
[11 empty] | SPEC. NO. |  |  |  |  | REV.
0
[7 empty] | (Thermal Mass Flow Meter) |  |  |  | CONTRACT |  |  |  |  | DATE
CLIENT |  | : | Samsung Electronics | [12 empty] | 2016.03.06
PROJECT |  | : |  |  |  |  | NO | BY | DATE | REVISION | REQ. or P.O
JOB NO. |  | : |  |  |  |  | 0 |  | 2016.03.06 | FOR APPROVAL
LOCATION |  | : | Compressed & Process Air line | [7 empty] | BY |  | CHK'D |  |  | APPR.
GENERAL
1 | Tag Number |  |  |  |  | FT-2AC1 |  |  | FT-2AC2 |  |  | FT-2AC3
2 | Quantity(Set) |  |  |  |  | 1 |  |  | 1 |  |  | 1
3 | Service
4 | Line No. & Sch. No |  |  |  |  | 12"(300A) & 10 |  |  | 12"(300A) & 10 |  |  | 12"(300A) & 10
SERIVCE CONDITION
5 | Fluid |  |  |  |  | Compressed Air |  |  | Compressed Air |  |  | Compressed Air
6 | Flow Rate(Nm3/h) |  |  |  | Nor. | 7500 |  |  | 7500 |  |  | 7500
Max.
7 | Pressure(kg/cm2.G) |  |  |  | Nor. | 8 |  |  | 8 |  |  | 8
Max.
8 | Temperature(℃) |  |  |  | Nor. | AMB |  |  | AMB |  |  | AMB
Max.
9 | Sp/gr(kg/m3) |  |  |  |  | 1000 |  |  | 1000 |  |  | 1000
10 | Viscosity |  |  |  |  | N/A |  |  | N/A |  |  | N/A
11 | Molecular Weight |  |  |  |  | 29 |  |  | 29 |  |  | 29
FLOW SENSOR
11 | Type |  |  |  |  | Insertion |  |  | Insertion |  |  | Insertion
12 | Velocity(m/s)
13 | Insert Length (L09) |  |  |  |  | 230mm |  |  | 230mm |  |  | 230mm
14 | Connection Type |  |  |  |  | Compression Fitting |  |  | Compression Fitting |  |  | Compression Fitting
15 | Connection Size & Rating |  |  |  |  | 3/4"NPT + 3/4" Tube & 10Bar |  |  | 3/4"NPT + 3/4" Tube & 10Bar |  |  | 3/4"NPT + 3/4" Tube & 10Bar
16 | Material |  |  | Sensor Probe |  | Ceramic+SUS303 |  |  | Ceramic+SUS303 |  |  | Ceramic+SUS303
|  |  |  | Protection tube |  | SUS303 |  |  | SUS303 |  |  | SUS303
|  |  |  | Comp' Fitting |  | SUS316 |  |  | SUS316 |  |  | SUS316
17 | Temperature(℃) |  |  |  | Min. | -40 |  |  | -40 |  |  | -40
[5 empty] | Max. | 150 |  |  | 150 |  |  | 150
18 | Accuracy |  |  |  |  | ±0.5% F.S (Reading : +/-0.5% F.S) |  |  | ±0.5% F.S (Reading : +/-0.5% F.S) |  |  | ±0.5% F.S (Reading : +/-0.5% F.S)
19 | Flow Direction |  |  |  |  | Horizontal -> Free |  |  | Horizontal -> Free |  |  | Horizontal -> Free
TRANSIMITTER
20 | Type |  |  |  |  | Program Smart |  |  | Program Smart |  |  | Program Smart
21 | Power Input |  |  |  |  | 24VDC, max. 200mA |  |  | 24VDC, max. 200mA |  |  | 24VDC, max. 200mA
22 | Output Signal |  |  |  |  | 4~20mA DC & Pulse |  |  | 4~20mA DC & Pulse |  |  | 4~20mA DC & Pulse
23 | Interface |  |  |  |  | MOD-BUS RS-485 |  |  | MOD-BUS RS-485 |  |  | MOD-BUS RS-485
24 | Enclosure |  |  |  |  | IP 67 |  |  | IP 67 |  |  | IP 67
25 | Display(LCD) |  |  |  |  | Flow Rate & Total, Velocity |  |  | Flow Rate & Total, Velocity |  |  | Flow Rate & Total, Velocity
26 | Housing Mat'l |  |  |  |  | Al.Casting |  |  | Al.Casting |  |  | Al.Casting
27 | Scale Range |  |  |  |  | 0 ~ 8000 Nm3/h |  |  | 0 ~ 8000 Nm3/h |  |  | 0 ~ 8000 Nm3/h
28 | Compensation : Press' & Temp' |  |  |  |  | Yes |  |  | Yes |  |  | Yes
ACCESSORIES
29 | Compression Fitting |  |  |  |  | Yes |  |  | Yes |  |  | Yes
30 | Remote Cable(30m) |  |  |  |  | Not |  |  | Not |  |  | Not
31 | Ball Valve |  |  |  |  | Not |  |  | Not |  |  | Not
32 | Option 1 :
MANUFACTURER
33 | M.F.R |  |  |  |  | Golden Rules |  |  | Golden Rules |  |  | Golden Rules
34 | Model No. |  |  |  |  | KC-2610GI |  |  | KC-2610GI |  |  | KC-2610GI
Notes :
MASS FLOW METERS
Golden Rules Co., Ltd.