## 1
[7 empty] | MASS FLOW METER |  |  |  | SHEET |  | 1 | OF |  | 1
[11 empty] | SPEC. NO. |  |  |  | REV.
0
[7 empty] | (FN- Mass Flow Meter) |  |  |  | CONTRACT |  |  |  | DATE
CLIENT |  | : | KOGAS통영기지본부 | [11 empty] | 2020.01.17
PROJECT |  | : | LSMGO MSDS |  |  |  | NO | BY | DATE | REVISION | REQ. or P.O
JOB NO. |  | : |  |  |  |  | 0 |  | 2020.01.17 | FOR APPROVAL
LOCATION |  | : | 선박디젤 수송라인 유량 측정용 | [7 empty] | BY | CHK'D |  |  | APPR.
GENERAL
1 | Tag Number
2 | Quantity(Set) |  |  |  |  | 2
3 | Service
4 | Line No. & Sch. No |  |  |  |  | 10"(250A)
SERIVCE CONDITION
5 | Fluid |  |  |  |  | Diesel Oil
6 | Flow Rate(m3/h) |  |  |  | Nor.
[5 empty] | Max. | 500
7 | Pressure(kg/cm2) |  |  |  | Min. | 0.9
[5 empty] | Max. | 11
8 | Temperature(℃) |  |  |  | Nor. | 25
[5 empty] | Max. | 60
9 | Sp/gr |  |  |  |  | kg/m3
10 | Viscosity(CST) |  |  |  |  | 1.5~6.0
FLOW SENSOR
11 | Type |  |  |  |  | Inline
12 | Flow Velocity |  |  |  |  | 0 ~ 100 m/s
13 | Length (C to C) |  |  |  |  | 500 mm
14 | Connection Type |  |  |  |  | Flange
15 | Flange Size & Rating |  |  |  |  | 10" ANSI 150# RF
16 | Material |  |  | Sensor |  | SUS304
|  |  |  | Flange |  | SUS304
17 | Temperature(℃) |  |  |  | Min. | -20
[5 empty] | Max. | 80
18 | Accuracy |  |  |  |  | ±1.0% R.D (Option: ±0.5% R.D)
19 | Flow Direction |  |  |  |  | Horizontal : Left -> Right
TRANSIMITTER
20 | Type |  |  |  |  | Program Smart & Integral
21 | Power Input |  |  |  |  | 24VDC, max. 100mA
22 | Output Signal |  |  |  |  | 4~20mA DC
23 | Interface |  |  |  |  | MOD-BUS RS-485
24 | Enclosure |  |  |  |  | Ex d IIC T6 (IP67) Atex
25 | Display(Rate&Total) |  |  |  |  | Volume,Mass,Density,Temp',Press'
26 | Housing Mat'l |  |  |  |  | Al.Casting
27 | Scale Range(m3/h) |  |  |  |  | 0 ~ 500
28 | Compensation(P & T) |  |  |  |  | Yes
ACCESSORIES
29 | Transmitter Bracket Assy |  |  |  |  | Yes
30 | With Ex-proof Indicator box |  |  |  |  | Yes
31 | W/ Installation & Operating |  |  |  |  | Yes
32 | Option 1 :
MANUFACTURER
33 | M.F.R |  |  |  |  | Golden Rules
34 | Model No. |  |  |  |  | KC-7730OP-FM153B
Notes :
현장 방폭형 인디케이터 박스 설치 및 유량계 시운전 포함
MASS FLOW METERS
Golden Rules Co., Ltd.