## 1
[7 empty] | MASS FLOW METER |  |  |  | SHEET |  | 1 | OF |  | 1
[11 empty] | SPEC. NO. |  |  |  | REV.
0
[7 empty] | (FN- Mass Flow Meter) |  |  |  | CONTRACT |  |  |  | DATE
CLIENT |  | : | Samsung Engineering | [11 empty] | 2022.02.17
PROJECT |  | : | 바이오가스 플랜트 |  |  |  | NO | BY | DATE | REVISION | REQ. or P.O
JOB NO. |  | : |  |  |  |  | 0 |  | 2022.02.17 | FOR APPROVAL
LOCATION |  | : | [8 empty] | BY | CHK'D |  |  | APPR.
GENERAL
1 | Tag Number
2 | Quantity(Set) |  |  |  |  | 1 |  |  | 1
3 | Service
4 | Line No. & Sch. No |  |  |  |  | 8"(200A) |  |  | 6"(150A)
SERIVCE CONDITION
5 | Fluid |  |  |  |  | Bio Gas |  |  | Bio Gas
6 | Flow Rate(Nm3/h) |  |  |  | Min. | 100 |  |  | 100
[5 empty] | Max. | 3000 |  |  | 3000
7 | Pressure(mmH2O) |  |  |  | Min. | 50 |  |  | 50
[5 empty] | Max. | 300 |  |  | 300
8 | Temperature(℃) |  |  |  | Nor. | 30 |  |  | 30
[5 empty] | Max. | 35 |  |  | 35
9 | Pressure Loss(bar) |  |  |  |  | 0.1~0.2 |  |  | 0.1~0.2
10 | Sp/gr (kg/m3) |  |  |  |  | Calculation Reference(?) |  |  | Calculation Reference(?)
10 | Viscosity(CST)
FLOW BODY
11 | Type |  |  |  |  | Inline |  |  | Inline
12 | Flow Velocity |  |  |  |  | 0.1 ~ 100 m/s |  |  | 0.1 ~ 100 m/s
13 | Length (L) |  |  |  |  | 300 |  |  | 300
14 | Connection Type |  |  |  |  | JIS Flange |  |  | JIS Flange
15 | Flange Size & Rating |  |  |  |  | 200A JIS 10K RF |  |  | 150A JIS 10K RF
16 | Material |  |  | D/P Sensor |  | SUS316 |  |  | SUS316
|  |  |  | Orifice Plate |  | SUS304 |  |  | SUS304
|  |  |  | Flange |  | SUS304 |  |  | SUS304
17 | Temperature(℃) |  |  |  | Min. | -40 |  |  | -40
[5 empty] | Max. | 100 |  |  | 100
18 | Accuracy |  |  |  |  | ±0.1% F.S |  |  | ±0.1% F.S
19 | Flow Direction |  |  |  |  | Horizontal : Left -> Right |  |  | Horizontal : Left -> Right
TRANSIMITTER
20 | Type |  |  |  |  | Program Smart & Integral |  |  | Program Smart & Integral
21 | Power Input |  |  |  |  | 24VDC, max. 100mA |  |  | 24VDC, max. 100mA
22 | Output Signal |  |  |  |  | 4~20mA DC |  |  | 4~20mA DC
23 | Interface |  |  |  |  | MOD-BUS RS-485 |  |  | MOD-BUS RS-485
24 | Enclosure |  |  |  |  | Ex d IIC T6 (IP67), Atex |  |  | Ex d IIC T6 (IP67), Atex
25 | Display(Rate&Total) |  |  |  |  | Volume,Mass,Density,Temp',Press' |  |  | Volume,Mass,Density,Temp',Press'
26 | Housing Mat'l |  |  |  |  | Al.Casting |  |  | Al.Casting
27 | Scale Range(Nm3/h) |  |  |  |  | 0 ~ 3,000 |  |  | 0 ~ 3,000
28 | Compensation(P & T) |  |  |  |  | Yes |  |  | Yes
ACCESSORIES
29 | Transmitter Bracket Assy |  |  |  |  | Not |  |  | Not
30 | With Ex-proof Indicator box |  |  |  |  | Not |  |  | Not
31 | W/ Installation & Operating |  |  |  |  | Not |  |  | Not
32 | Option 1 :
MANUFACTURER
33 | M.F.R |  |  |  |  | Golden Rules |  |  | Golden Rules
34 | Model No. |  |  |  |  | KC-7730B-FM153BEx |  |  | KC-7730B-FM153BEx
Notes :
MASS FLOW METERS
Golden Rules Co., Ltd.