## 1
[5 empty] | MASS FLOW METER |  |  |  | SHEET |  | 1 | OF |  | 1
[9 empty] | SPEC. NO. |  |  |  | REV.
0
[5 empty] | (Venturi type Mass Flow Meter) |  |  |  | CONTRACT |  |  |  | DATE
CLIENT |  | : | 에스코텍㈜ | [9 empty] | 2021.04.21
PROJECT |  | : | Venturi tube Mass Flowmeter |  | NO | BY | DATE | REVISION | REQ. or P.O
JOB NO. |  | : |  |  | 0 |  | 2021.04.21 | FOR APPROVAL
LOCATION |  | : | ㈜롯데케미칼 | [5 empty] | BY | CHK'D |  |  | APPR.
UPSTREAM FLUID
1 | Temperature |  |  | 17 | [ ℃ ]
2 | Absolute Pressure |  |  | 101.3 | [ kPa ]
3 | Density |  |  | 1.216 | [ kg/m3 ]
4 | Viscosity |  |  | 18.101 | [ μPa-s ]
5 | Enthalpy |  |  | 290.396 | [ kJ/kg ]
6 | Isobaric Specific Heat |  |  | 1.006 | [ kJ/kgK ]
7 | Flow rate |  |  | 50300 | [ kg/h ]
8 | Flow Range[kg/h(m3/h)] |  |  | 0.000~50300.000
9 | Velocity |  |  | 6.297 | [ m/s ]
10
Pipe
11 | Pipe Material |  |  | STS304
12 | Standard |  |  | Custom
13 | Schedule |  |  | 40S
14 | Size
Connection
15 | Material
16 | Standard |  |  | Custom
17 | Grade
18 | Type
Requirments
19 | Contro Mode |  |  | OFF
20 | Display |  |  | [ kg/h(m3/h) ]
21 | Explosion |  |  | KGS,Atex(Ex d IIC T6: IP67)
22 | Output |  |  | 4 - 20mA, 4-Wire
23 | Network |  |  | Modbus
24 | Power |  |  | DC 24V, 100mA
25 | Install Location |  |  | Indoor
26 | Casing Direction |  |  | Top
27 | Flow Direction |  |  | Left to Right
28 | Manifold Valve |  |  | No
29 | Condensate Pot |  |  | No
30 | Flow Conditioner |  |  | No
31 | Composition Ratio |  |  | Fixed
Notes :
1,524 * 1524 사각덕트용 벤츄리 튜브
MASS FLOW METERS
Golden Rules Co., Ltd.